# POLICY:	EMERGENCY LIGHTING TESTING

# PURPOSE:

Quality Behavioral Health (QBH) provides for patient and staff safety by establishing mechanisms to minimize risk.

# PROCEDURS:

# The Safety Officer, or designee, shall test emergency lighting on a monthly basis and document findings on the Emergency Lighting Testing Log (available from the Office Manager, or from the Administrative Assistant.

# There is a test button on the lighting unit itself.  When the button is pushed, if the light comes on, the unit is working properly.

# The monthly test is to be conducted for 30 seconds and the annual test is to be conducted for 1.5 hours. Failed tests will be documented and retest will be performed after resolution of failure.

- All emergency light batteries will be randomly tested annually, in addition to the normal tests.

- After any storm or power outage all emergency lights and lighted exit signs must be checked to see that the batteries are working.

# EVALUATION:

- The Safety Officer shall review and, if needed, revise this policy annually and submit to the Clinical Committee for approval.

# RELATED POLICIES/FORMS:

# Safety Inspection Surveillance Checklist

Emergency Lighting Testing Log

Utilities Management Plan

EXHIBIT A:    EMERGENCY LIGHT TESTING

In the event that it is necessary to check the emergency lights of lighted exit signs, the following procedure will be observed:

To check emergency lights press and hold the test button for five (5) seconds. If the light comes on the battery is charged and working. If the light does not come on, test again. If the light is still not working, then the battery is dead and must be replaced IMMEDIATELY.

For testing the lighted emergency light, press the test button. When a battery is charged and working properly the light will blink quickly, but only once. If you are uncertain, test again. If the light does not blink after two (2) attempts the battery needs to be replaced IMMEDIATELY.

If replacement batteries are not on hand, acquire batteries promptly and replace them.

If the power is out to the facility for more than two hours the battery will be dead or nearly so and must be replaced promptly.