# POLICY:		LIFE (FIRE) SAFETY EQUIPMENT TESTING

It is the policy of Quality Behavioral Health, Inc. (QBH) to maintain, test, and inspect all life safety components in QBH Facilities.

PURPOSE:

The purpose of testing life safety equipment is to establish mechanisms to support the proper working order of all fire related devices for the safety of all staff, consumers, and visitors.

DEFINITIONS:

- Life safety equipment – any equipment designed to protect consumers, staff, visitors, and property from fire.

- Fire alarm – any device that will sound an alarm in case of fire, whether activated manually or by smoke and/or heat.

- Detectors – any device that sets in motion fire control, such as a smoke detector, sprinkler, automatic door closer, etc.

PROCEDURES:

STATEMENT OF CONDITIONS

- Each building in which consumers are housed or receive treatment will have a comprehensive statement of conditions (SOC), available to JC, which describes the current condition of the building’s structural features of fire protection.

INSPECTION AND TESTING OF FIRE RELATED EQUIPMENT, SYSTEMS, AND COMPONENTS

  - The Safety Officer or designee shall inspect and test fire equipment according to these guidelines:

    - Signal devices – quarterly.

    - Valve tamper switches and water flow devices – semi-annually.

    - Manual fire alarms, smoke detectors, heat/duct detectors – annually.

      - Fire alarm pull stations are inspected by looking at the handle in the pull station to see that it is straight up.

      - Fire detectors are inspected by looking at them and checking that the red light is blinking every 30 seconds. Fire detectors are located in every department lobby and hall.

    - Audible and visible occupant alarm systems – annually.

    - Off premises emergency notification transmission equipment – quarterly.

    - Water-based automatic fire extinguishing system fire pumps – weekly under no-flow condition; annually under flow condition (by contractor).

    - Water-based automatic fire extinguishing storage tanks high and low water level test – semi-annually (during cold weather, low water level test monthly) by contractor.

    - Water-based automatic fire extinguishing main drain test – annually at all system risers (by contractor).

    - Water-based automatic fire extinguishing fire department connections – quarterly.

    - Portable extinguishers are clearly identified, maintained annually (once a year, every twelve months plus or minus twenty days) by contractor, and inspected monthly.

    - Standpipe occupant hoses hydrostatically tested – 5 years after install, then every three years (thirty-six months plus or minus thirty days), with water flow tests every 5 years sixty (months plus or minus thirty days) by contractor.

# Emergency lighting – The Safety Officer or designee shall test emergency lighting on a monthly (30-day intervals/12 times a year or once per month) basis and document findings on the Inspection, Testing, and Preventative Maintenance Logs.

- There is a test button on the lighting unit itself. When the button is pushed, if the light comes on, the unit is working properly.

- The monthly (30-day intervals/12 times a year or once per month) test is to be conducted for 30 seconds and the annual (once a year, every twelve months plus or minus thirty days) test is to be conducted for 1.5 hours. Failed tests will be documented and retest will be performed after resolution of failure.

- 10% of all emergency light batteries will be randomly tested annually (once a year, every twelve months plus or minus thirty days) in addition to the normal tests.

- After any storm or power outage, all emergency lights and lighted exit signs must be checked to see that the batteries are working.

# The Safety Officer or designee shall test battery powered smoke detectors on a monthly basis and replace weak or dead batteries and document findings on a Battery Testing Report Log. ALL smoke detector batteries will be replaced at least annually and documented on the battery testing form.

# There is a test button on the smoke detector. If alarm sounds when the button is pushed, the unit is working properly.

# To remove the battery, twist the cover in a counter clockwise direction to expose the battery. Simply remove the battery and replace with a new battery at least annually (once a year, every twelve months plus or minus ten days).

- Old/dead batteries are to be disposed of with the other hazmat materials.

RECORD KEEPING

  - The Safety Officer will maintain a manual of schedules and test performance reports for fire-detection equipment.

  - The location of all manually activated fire alarm pulls are noted on posted evacuation plans.

TRAINING

  - Training on operational use of fire equipment is provided to staff at orientation and annually as part of the yearly re-orientation.

  - Ongoing skill and knowledge is evaluated as part of fire drills.

EVALUATION:

- The Safety Officer will review and revise, if necessary, annually (once a year, every twelve months plus or minus thirty days), or as needed when circumstances change. The revised plan and plan evaluation will be submitted to the Clinical Committee for approval.

RELATED POLICIES/FORMS:

Life (Fire) Safety Plan

Fire Equipment Inspection Log

Safety Inspection Checklist

Battery Testing Report Log

Inspection, Testing and Preventative Maintenance Log